## Registers - group 1
Neuron L203
Registers - group 1
Register Address
Via Unit 0 | Via Unit 1 | R/W | Data Type | Content | Bit Nr. | Category
0 | 0 | R | MixedBits | Digital Inputs | 0 | Basic
|  |  |  | Digital Input 1.1 | 0 | Basic
|  |  |  | Digital Input 1.2 | 1 | Basic
|  |  |  | Digital Input 1.3 | 2 | Basic
|  |  |  | Digital Input 1.4 | 3 | Basic
1 | 1 | RW | MixedBits | Digital Outputs | 0 | Basic
|  |  |  | Digital Output 1.1 | 0 | Basic
|  |  |  | Digital Output 1.2 | 1 | Basic
|  |  |  | Digital Output 1.3 | 2 | Basic
|  |  |  | Digital Output 1.4 | 3 | Basic
2 | 2 | RW | Word | Analog Output (raw value) 1.1 |  | Obsolete
3 | 3 | R | Word | Analog Input (raw value) 1.1 |  | Obsolete
4 | 4 | R | Word | Analog Input/Output (raw value) 1.1 |  | Obsolete
5 | 5 | R | Word | VRefInt of MCU |  | Expert
6 | 6 | RW | MixedBits | Group MasterWatchDog (MWD) Status |  | Advanced
|  |  |  | MWD Enable | 0 | Advanced
|  |  |  | MWD Reboot Detected | 1 | Advanced
7 | 7 | R | Word | Length of RS485 TX Queue 1.1 |  | Obsolete
8 - 9 | 8 - 9 | RW | DWord | Counter of Digital Input 1.1 |  | Basic
10 - 11 | 10 - 11 | RW | DWord | Counter of Digital Input 1.2 |  | Basic
12 - 13 | 12 - 13 | RW | DWord | Counter of Digital Input 1.3 |  | Basic
14 - 15 | 14 - 15 | RW | DWord | Counter of Digital Input 1.4 |  | Basic
16 | 16 | RW | Word | PWM Duty Cycle of DO 1.1 |  | Basic
17 | 17 | RW | Word | PWM Duty Cycle of DO 1.2 |  | Basic
18 | 18 | RW | Word | PWM Duty Cycle of DO 1.3 |  | Basic
19 | 19 | RW | Word | PWM Duty Cycle of DO 1.4 |  | Basic
20 | 20 | RW | MixedBits | User-programmable LED states | 0 | Basic
|  |  |  | User LED 1.1 | 0 | Basic
|  |  |  | User LED 1.2 | 1 | Basic
|  |  |  | User LED 1.3 | 2 | Basic
|  |  |  | User LED 1.4 | 3 | Basic
21 | 21 | RW | MixedBits | Synchronised Digital Outputs/Relay Outputs | 0 | Advanced
|  |  |  | Synchronised DO/RO 1.1 | 0 | Advanced
|  |  |  | Synchronised DO/RO 1.2 | 1 | Advanced
|  |  |  | Synchronised DO/RO 1.3 | 2 | Advanced
|  |  |  | Synchronised DO/RO 1.4 | 3 | Advanced
22 | 22 | RW | MixedBits | Synchronised Digital Output/Relay Output Locks | 0 | Advanced
|  |  |  | Synchronised DO/RO Lock 1.1 | 0 | Advanced
|  |  |  | Synchronised DO/RO Lock 1.2 | 1 | Advanced
|  |  |  | Synchronised DO/RO Lock 1.3 | 2 | Advanced
|  |  |  | Synchronised DO/RO Lock 1.4 | 3 | Advanced
| 100 - 101 | RW | DWord | (Internal) RS485 Full Mode Configuration 1.1 |  | Obsolete
| 500 | RW | Word | RS485 TERMIOS CFlags 1.1 |  | Expert
| 501 | RW | Word | RS485 TERMIOS LFlags 1.1 |  | Expert
| 502 | RW | Word | RS485 TERMIOS IFlags 1.1 |  | Expert
| 503 | RW | Word | RS485 TERMIOS LDisc 1.1 |  | Expert
| 504 | RW | Word | RS485 ModBus Timeout 1.1 |  | Basic
505 | 505 | W | Word | Reserved - Do Not Use |  | Reserved
506 | 506 | W | Word | Reserved - Do Not Use |  | Reserved
507 | 507 | W | Word | Reserved - Do Not Use |  | Reserved
508 | 508 | W | Word | Reserved - Do Not Use |  | Reserved
509 | 509 | W | Word | Reserved - Do Not Use |  | Reserved
| 510 | RW | Word | (Internal) Stored Firmware Version |  | Expert
| 511 | RW | Word | (Internal) Stored Firmware Revision |  | Expert
| 512 | RW | Word | (Internal) Stored Base Firmware Revision |  | Expert
| 513 | RW | Word | (Internal) Stored Expanded Flash Magic Value |  | Expert
| 514 | RW | Word | (Internal) Stored PCB Revision |  | Expert
| 515 | RW | Word | (Internal) Stored PCB Serial Number |  | Expert
| 516 | RW | Word | (Internal) Stored HW Revision Number |  | Expert
1000 | 1000 | R | Word | Firmware Version |  | Expert
1001 | 1001 | R | Word | Number of I/Os |  | Advanced
|  |  |  | Number of DIs | 0 - 7 | Advanced
|  |  |  | Number of DOs | 8 - 15 | Advanced
1002 | 1002 | R | Word | Number of peripherals |  | Advanced
|  |  |  | Number of internal RS485 lines | 0 - 3 | Advanced
|  |  |  | Number of AOs | 4 - 7 | Advanced
|  |  |  | Number of AIs | 8 - 15 | Advanced
1003 | 1003 | R | Word | Firmware ID |  | Expert
1004 | 1004 | R | Word | Hardware ID |  | Expert
1005 - 1006 | 1005 - 1006 | R | DWord | PCB Serial Number |  | Expert
1007 | 1007 | RW | Word | Interrupt Mask |  | Expert
|  |  |  | RS485 RX queue not empty | 0 | Expert
|  |  |  | RS485 TX queue empty | 1 | Expert
|  |  |  | RS485 ModBus RX frame finished | 2 | Expert
|  |  |  | Digital Input changed state | 3 | Expert
1008 | 1008 | RW | Word | Group MasterWatchDog (MWD) Timeout (in 1ms) |  | Advanced
1009 | 1009 | R | Word | VRef of MCU |  | Expert
1010 | 1010 | RW | Word | Debounce time (in 100us) for DI 1.1 |  | Advanced
1011 | 1011 | RW | Word | Debounce time (in 100us) for DI 1.2 |  | Advanced
1012 | 1012 | RW | Word | Debounce time (in 100us) for DI 1.3 |  | Advanced
1013 | 1013 | RW | Word | Debounce time (in 100us) for DI 1.4 |  | Advanced
1014 | 1014 | RW | MixedBits | Enable DirectSwitch functionality | 0 | Basic
|  |  |  | Enable DirectSwitch on DI 1.1 | 0 | Basic
|  |  |  | Enable DirectSwitch on DI 1.2 | 1 | Basic
|  |  |  | Enable DirectSwitch on DI 1.3 | 2 | Basic
|  |  |  | Enable DirectSwitch on DI 1.4 | 3 | Basic
1015 | 1015 | RW | MixedBits | Invert DirectSwitch Polarity | 0 | Basic
|  |  |  | Invert DirectSwitch Polarity on DI 1.1 | 0 | Basic
|  |  |  | Invert DirectSwitch Polarity on DI 1.2 | 1 | Basic
|  |  |  | Invert DirectSwitch Polarity on DI 1.3 | 2 | Basic
|  |  |  | Invert DirectSwitch Polarity on DI 1.4 | 3 | Basic
1016 | 1016 | RW | MixedBits | Enabled DirectSwitch Toggle | 0 | Basic
|  |  |  | Enable DirectSwitch Toggle on DI 1.1 | 0 | Basic
|  |  |  | Enable DirectSwitch Toggle on DI 1.2 | 1 | Basic
|  |  |  | Enable DirectSwitch Toggle on DI 1.3 | 2 | Basic
|  |  |  | Enable DirectSwitch Toggle on DI 1.4 | 3 | Basic
1017 | 1017 | RW | Word | PWM Group prescaler |  | Basic
1018 | 1018 | RW | Word | PWM Group cycle length |  | Basic
1019 | 1019 | RW | Word | Analog Output Configuration(U/I/R-measure) 1.1 |  | Basic
1020 | 1020 | RW | Word | Analog Output Voltage deviation 1.1 |  | Expert
1021 | 1021 | RW | Word | Analog Output Voltage offset 1.1 |  | Expert
1022 | 1022 | RW | Word | Analog Output Current deviation 1.1 |  | Expert
1023 | 1023 | RW | Word | Analog Output Current offset 1.1 |  | Expert
1024 | 1024 | RW | Word | Analog Input Configuration(U/I) 1.1 |  | Basic
1025 | 1025 | RW | Word | Analog Input Voltage deviation 1.1 |  | Expert
1026 | 1026 | RW | Word | Analog Input Voltage offset 1.1 |  | Expert
1027 | 1027 | RW | Word | Analog Input Current deviation 1.1 |  | Expert
1028 | 1028 | RW | Word | Analog Input Current offset 1.1 |  | Expert
1029 | 1029 | RW | Word | Analog Input/Output Voltage deviation (input side) 1.1 |  | Expert
1030 | 1030 | RW | Word | Analog Input/Output Voltage offset (input side) 1.1 |  | Expert
1031 | 1031 | RW | MixedBits | RS485-1.1 Configuration |  | Obsolete
|  |  |  | Baud rate | 0 - 12 | Obsolete
|  |  |  | Parity enable | 13 | Obsolete
|  |  |  | Parity-0=Even, 1=Odd | 14 | Obsolete
|  |  |  | Modbus RTU support enabled (interrupt) | 15 | Obsolete
| 2000 - 2219 | W | Word | Reserved - Do Not Use |  | Reserved
3000 - 3001 | 3000 - 3001 | RW | Real | Analog Output value 1.1 |  | Basic
3002 - 3003 | 3002 - 3003 | R | Real | Analog Input value 1.1 |  | Basic
3004 - 3005 | 3004 - 3005 | R | Real | (Internal) Analog Output measured voltage value 1.1 |  | Expert

## Registers - group 2
Neuron L203
Registers - group 2
Register Address
Via Unit 0 | Via Unit 2 | R/W | Data Type | Content | Bit Nr. | Category
100 | 0 | R | MixedBits | Digital Inputs | 0 | Basic
|  |  |  | Digital Input 2.1 | 0 | Basic
|  |  |  | Digital Input 2.2 | 1 | Basic
|  |  |  | Digital Input 2.3 | 2 | Basic
|  |  |  | Digital Input 2.4 | 3 | Basic
|  |  |  | Digital Input 2.5 | 4 | Basic
|  |  |  | Digital Input 2.6 | 5 | Basic
|  |  |  | Digital Input 2.7 | 6 | Basic
|  |  |  | Digital Input 2.8 | 7 | Basic
|  |  |  | Digital Input 2.9 | 8 | Basic
|  |  |  | Digital Input 2.10 | 9 | Basic
|  |  |  | Digital Input 2.11 | 10 | Basic
|  |  |  | Digital Input 2.12 | 11 | Basic
|  |  |  | Digital Input 2.13 | 12 | Basic
|  |  |  | Digital Input 2.14 | 13 | Basic
|  |  |  | Digital Input 2.15 | 14 | Basic
|  |  |  | Digital Input 2.16 | 15 | Basic
101 | 1 | RW | MixedBits | Relay Outputs | 0 | Basic
|  |  |  | Relay Output 2.1 | 0 | Basic
|  |  |  | Relay Output 2.2 | 1 | Basic
|  |  |  | Relay Output 2.3 | 2 | Basic
|  |  |  | Relay Output 2.4 | 3 | Basic
|  |  |  | Relay Output 2.5 | 4 | Basic
|  |  |  | Relay Output 2.6 | 5 | Basic
|  |  |  | Relay Output 2.7 | 6 | Basic
|  |  |  | Relay Output 2.8 | 7 | Basic
|  |  |  | Relay Output 2.9 | 8 | Basic
|  |  |  | Relay Output 2.10 | 9 | Basic
|  |  |  | Relay Output 2.11 | 10 | Basic
|  |  |  | Relay Output 2.12 | 11 | Basic
|  |  |  | Relay Output 2.13 | 12 | Basic
|  |  |  | Relay Output 2.14 | 13 | Basic
102 | 2 | RW | MixedBits | Group MasterWatchDog (MWD) Status |  | Advanced
|  |  |  | MWD Enable | 0 | Advanced
|  |  |  | MWD Reboot Detected | 1 | Advanced
103 - 104 | 3 - 4 | RW | DWord | Counter of Digital Input 2.1 |  | Basic
105 - 106 | 5 - 6 | RW | DWord | Counter of Digital Input 2.2 |  | Basic
107 - 108 | 7 - 8 | RW | DWord | Counter of Digital Input 2.3 |  | Basic
109 - 110 | 9 - 10 | RW | DWord | Counter of Digital Input 2.4 |  | Basic
111 - 112 | 11 - 12 | RW | DWord | Counter of Digital Input 2.5 |  | Basic
113 - 114 | 13 - 14 | RW | DWord | Counter of Digital Input 2.6 |  | Basic
115 - 116 | 15 - 16 | RW | DWord | Counter of Digital Input 2.7 |  | Basic
117 - 118 | 17 - 18 | RW | DWord | Counter of Digital Input 2.8 |  | Basic
119 - 120 | 19 - 20 | RW | DWord | Counter of Digital Input 2.9 |  | Basic
121 - 122 | 21 - 22 | RW | DWord | Counter of Digital Input 2.10 |  | Basic
123 - 124 | 23 - 24 | RW | DWord | Counter of Digital Input 2.11 |  | Basic
125 - 126 | 25 - 26 | RW | DWord | Counter of Digital Input 2.12 |  | Basic
127 - 128 | 27 - 28 | RW | DWord | Counter of Digital Input 2.13 |  | Basic
129 - 130 | 29 - 30 | RW | DWord | Counter of Digital Input 2.14 |  | Basic
131 - 132 | 31 - 32 | RW | DWord | Counter of Digital Input 2.15 |  | Basic
133 - 134 | 33 - 34 | RW | DWord | Counter of Digital Input 2.16 |  | Basic
135 | 35 | W | Word | Reserved - Do Not Use |  | Reserved
136 | 36 | W | Word | Reserved - Do Not Use |  | Reserved
137 | 37 | W | Word | Reserved - Do Not Use |  | Reserved
138 | 38 | W | Word | Reserved - Do Not Use |  | Reserved
139 | 39 | RW | MixedBits | Synchronised Digital Outputs/Relay Outputs | 0 | Advanced
|  |  |  | Synchronised DO/RO 2.1 | 0 | Advanced
|  |  |  | Synchronised DO/RO 2.2 | 1 | Advanced
|  |  |  | Synchronised DO/RO 2.3 | 2 | Advanced
|  |  |  | Synchronised DO/RO 2.4 | 3 | Advanced
|  |  |  | Synchronised DO/RO 2.5 | 4 | Advanced
|  |  |  | Synchronised DO/RO 2.6 | 5 | Advanced
|  |  |  | Synchronised DO/RO 2.7 | 6 | Advanced
|  |  |  | Synchronised DO/RO 2.8 | 7 | Advanced
|  |  |  | Synchronised DO/RO 2.9 | 8 | Advanced
|  |  |  | Synchronised DO/RO 2.10 | 9 | Advanced
|  |  |  | Synchronised DO/RO 2.11 | 10 | Advanced
|  |  |  | Synchronised DO/RO 2.12 | 11 | Advanced
|  |  |  | Synchronised DO/RO 2.13 | 12 | Advanced
|  |  |  | Synchronised DO/RO 2.14 | 13 | Advanced
140 | 40 | RW | MixedBits | Synchronised Digital Output/Relay Output Locks | 0 | Advanced
|  |  |  | Synchronised DO/RO Lock 2.1 | 0 | Advanced
|  |  |  | Synchronised DO/RO Lock 2.2 | 1 | Advanced
|  |  |  | Synchronised DO/RO Lock 2.3 | 2 | Advanced
|  |  |  | Synchronised DO/RO Lock 2.4 | 3 | Advanced
|  |  |  | Synchronised DO/RO Lock 2.5 | 4 | Advanced
|  |  |  | Synchronised DO/RO Lock 2.6 | 5 | Advanced
|  |  |  | Synchronised DO/RO Lock 2.7 | 6 | Advanced
|  |  |  | Synchronised DO/RO Lock 2.8 | 7 | Advanced
|  |  |  | Synchronised DO/RO Lock 2.9 | 8 | Advanced
|  |  |  | Synchronised DO/RO Lock 2.10 | 9 | Advanced
|  |  |  | Synchronised DO/RO Lock 2.11 | 10 | Advanced
|  |  |  | Synchronised DO/RO Lock 2.12 | 11 | Advanced
|  |  |  | Synchronised DO/RO Lock 2.13 | 12 | Advanced
|  |  |  | Synchronised DO/RO Lock 2.14 | 13 | Advanced
| 100 - 101 | RW | DWord | (Internal) RS485 Full Mode Configuration 2.1 |  | Obsolete
600 | 500 | W | Word | Reserved - Do Not Use |  | Reserved
601 | 501 | W | Word | Reserved - Do Not Use |  | Reserved
602 | 502 | W | Word | Reserved - Do Not Use |  | Reserved
603 | 503 | W | Word | Reserved - Do Not Use |  | Reserved
604 | 504 | W | Word | Reserved - Do Not Use |  | Reserved
605 | 505 | W | Word | Reserved - Do Not Use |  | Reserved
606 | 506 | W | Word | Reserved - Do Not Use |  | Reserved
607 | 507 | W | Word | Reserved - Do Not Use |  | Reserved
608 | 508 | W | Word | Reserved - Do Not Use |  | Reserved
609 | 509 | W | Word | Reserved - Do Not Use |  | Reserved
| 510 | RW | Word | (Internal) Stored Firmware Version |  | Expert
| 511 | RW | Word | (Internal) Stored Firmware Revision |  | Expert
| 512 | RW | Word | (Internal) Stored Base Firmware Revision |  | Expert
| 513 | RW | Word | (Internal) Stored Expanded Flash Magic Value |  | Expert
| 514 | RW | Word | (Internal) Stored PCB Revision |  | Expert
| 515 | RW | Word | (Internal) Stored PCB Serial Number |  | Expert
| 516 | RW | Word | (Internal) Stored HW Revision Number |  | Expert
1100 | 1000 | R | Word | Firmware Version |  | Expert
1101 | 1001 | R | Word | Number of I/Os |  | Advanced
|  |  |  | Number of DIs | 0 - 7 | Advanced
|  |  |  | Number of DOs | 8 - 15 | Advanced
1102 | 1002 | R | Word | Number of peripherals |  | Advanced
|  |  |  | Number of internal RS485 lines | 0 - 3 | Advanced
|  |  |  | Number of AOs | 4 - 7 | Advanced
|  |  |  | Number of AIs | 8 - 15 | Advanced
1103 | 1003 | R | Word | Firmware ID |  | Expert
1104 | 1004 | R | Word | Hardware ID |  | Expert
1105 - 1106 | 1005 - 1006 | R | DWord | PCB Serial Number |  | Expert
1107 | 1007 | RW | Word | Interrupt Mask |  | Expert
|  |  |  | RS485 RX queue not empty | 0 | Expert
|  |  |  | RS485 TX queue empty | 1 | Expert
|  |  |  | RS485 ModBus RX frame finished | 2 | Expert
|  |  |  | Digital Input changed state | 3 | Expert
1108 | 1008 | RW | Word | Group MasterWatchDog (MWD) Timeout (in 1ms) |  | Advanced
1109 | 1009 | R | Word | VRef of MCU |  | Expert
1110 | 1010 | RW | Word | Debounce time (in 100us) for DI 2.1 |  | Advanced
1111 | 1011 | RW | Word | Debounce time (in 100us) for DI 2.2 |  | Advanced
1112 | 1012 | RW | Word | Debounce time (in 100us) for DI 2.3 |  | Advanced
1113 | 1013 | RW | Word | Debounce time (in 100us) for DI 2.4 |  | Advanced
1114 | 1014 | RW | Word | Debounce time (in 100us) for DI 2.5 |  | Advanced
1115 | 1015 | RW | Word | Debounce time (in 100us) for DI 2.6 |  | Advanced
1116 | 1016 | RW | Word | Debounce time (in 100us) for DI 2.7 |  | Advanced
1117 | 1017 | RW | Word | Debounce time (in 100us) for DI 2.8 |  | Advanced
1118 | 1018 | RW | Word | Debounce time (in 100us) for DI 2.9 |  | Advanced
1119 | 1019 | RW | Word | Debounce time (in 100us) for DI 2.10 |  | Advanced
1120 | 1020 | RW | Word | Debounce time (in 100us) for DI 2.11 |  | Advanced
1121 | 1021 | RW | Word | Debounce time (in 100us) for DI 2.12 |  | Advanced
1122 | 1022 | RW | Word | Debounce time (in 100us) for DI 2.13 |  | Advanced
1123 | 1023 | RW | Word | Debounce time (in 100us) for DI 2.14 |  | Advanced
1124 | 1024 | RW | Word | Debounce time (in 100us) for DI 2.15 |  | Advanced
1125 | 1025 | RW | Word | Debounce time (in 100us) for DI 2.16 |  | Advanced
1126 | 1026 | RW | MixedBits | Enable DirectSwitch functionality | 0 | Basic
|  |  |  | Enable DirectSwitch on DI 2.1 | 0 | Basic
|  |  |  | Enable DirectSwitch on DI 2.2 | 1 | Basic
|  |  |  | Enable DirectSwitch on DI 2.3 | 2 | Basic
|  |  |  | Enable DirectSwitch on DI 2.4 | 3 | Basic
|  |  |  | Enable DirectSwitch on DI 2.5 | 4 | Basic
|  |  |  | Enable DirectSwitch on DI 2.6 | 5 | Basic
|  |  |  | Enable DirectSwitch on DI 2.7 | 6 | Basic
|  |  |  | Enable DirectSwitch on DI 2.8 | 7 | Basic
|  |  |  | Enable DirectSwitch on DI 2.9 | 8 | Basic
|  |  |  | Enable DirectSwitch on DI 2.10 | 9 | Basic
|  |  |  | Enable DirectSwitch on DI 2.11 | 10 | Basic
|  |  |  | Enable DirectSwitch on DI 2.12 | 11 | Basic
|  |  |  | Enable DirectSwitch on DI 2.13 | 12 | Basic
|  |  |  | Enable DirectSwitch on DI 2.14 | 13 | Basic
1127 | 1027 | RW | MixedBits | Invert DirectSwitch Polarity | 0 | Basic
|  |  |  | Invert DirectSwitch Polarity on DI 2.1 | 0 | Basic
|  |  |  | Invert DirectSwitch Polarity on DI 2.2 | 1 | Basic
|  |  |  | Invert DirectSwitch Polarity on DI 2.3 | 2 | Basic
|  |  |  | Invert DirectSwitch Polarity on DI 2.4 | 3 | Basic
|  |  |  | Invert DirectSwitch Polarity on DI 2.5 | 4 | Basic
|  |  |  | Invert DirectSwitch Polarity on DI 2.6 | 5 | Basic
|  |  |  | Invert DirectSwitch Polarity on DI 2.7 | 6 | Basic
|  |  |  | Invert DirectSwitch Polarity on DI 2.8 | 7 | Basic
|  |  |  | Invert DirectSwitch Polarity on DI 2.9 | 8 | Basic
|  |  |  | Invert DirectSwitch Polarity on DI 2.10 | 9 | Basic
|  |  |  | Invert DirectSwitch Polarity on DI 2.11 | 10 | Basic
|  |  |  | Invert DirectSwitch Polarity on DI 2.12 | 11 | Basic
|  |  |  | Invert DirectSwitch Polarity on DI 2.13 | 12 | Basic
|  |  |  | Invert DirectSwitch Polarity on DI 2.14 | 13 | Basic
1128 | 1028 | RW | MixedBits | Enabled DirectSwitch Toggle | 0 | Basic
|  |  |  | Enable DirectSwitch Toggle on DI 2.1 | 0 | Basic
|  |  |  | Enable DirectSwitch Toggle on DI 2.2 | 1 | Basic
|  |  |  | Enable DirectSwitch Toggle on DI 2.3 | 2 | Basic
|  |  |  | Enable DirectSwitch Toggle on DI 2.4 | 3 | Basic
|  |  |  | Enable DirectSwitch Toggle on DI 2.5 | 4 | Basic
|  |  |  | Enable DirectSwitch Toggle on DI 2.6 | 5 | Basic
|  |  |  | Enable DirectSwitch Toggle on DI 2.7 | 6 | Basic
|  |  |  | Enable DirectSwitch Toggle on DI 2.8 | 7 | Basic
|  |  |  | Enable DirectSwitch Toggle on DI 2.9 | 8 | Basic
|  |  |  | Enable DirectSwitch Toggle on DI 2.10 | 9 | Basic
|  |  |  | Enable DirectSwitch Toggle on DI 2.11 | 10 | Basic
|  |  |  | Enable DirectSwitch Toggle on DI 2.12 | 11 | Basic
|  |  |  | Enable DirectSwitch Toggle on DI 2.13 | 12 | Basic
|  |  |  | Enable DirectSwitch Toggle on DI 2.14 | 13 | Basic
1129 | 1029 | W | Word | Reserved - Do Not Use |  | Reserved
1130 | 1030 | W | Word | Reserved - Do Not Use |  | Reserved
| 2000 - 2219 | W | Word | Reserved - Do Not Use |  | Reserved

## Registers - group 3
Neuron L203
Registers - group 3
Register Address
Via Unit 0 | Via Unit 3 | R/W | Data Type | Content | Bit Nr. | Category
200 | 0 | R | MixedBits | Digital Inputs | 0 | Basic
|  |  |  | Digital Input 3.1 | 0 | Basic
|  |  |  | Digital Input 3.2 | 1 | Basic
|  |  |  | Digital Input 3.3 | 2 | Basic
|  |  |  | Digital Input 3.4 | 3 | Basic
|  |  |  | Digital Input 3.5 | 4 | Basic
|  |  |  | Digital Input 3.6 | 5 | Basic
|  |  |  | Digital Input 3.7 | 6 | Basic
|  |  |  | Digital Input 3.8 | 7 | Basic
|  |  |  | Digital Input 3.9 | 8 | Basic
|  |  |  | Digital Input 3.10 | 9 | Basic
|  |  |  | Digital Input 3.11 | 10 | Basic
|  |  |  | Digital Input 3.12 | 11 | Basic
|  |  |  | Digital Input 3.13 | 12 | Basic
|  |  |  | Digital Input 3.14 | 13 | Basic
|  |  |  | Digital Input 3.15 | 14 | Basic
|  |  |  | Digital Input 3.16 | 15 | Basic
201 | 1 | RW | MixedBits | Relay Outputs | 0 | Basic
|  |  |  | Relay Output 3.1 | 0 | Basic
|  |  |  | Relay Output 3.2 | 1 | Basic
|  |  |  | Relay Output 3.3 | 2 | Basic
|  |  |  | Relay Output 3.4 | 3 | Basic
|  |  |  | Relay Output 3.5 | 4 | Basic
|  |  |  | Relay Output 3.6 | 5 | Basic
|  |  |  | Relay Output 3.7 | 6 | Basic
|  |  |  | Relay Output 3.8 | 7 | Basic
|  |  |  | Relay Output 3.9 | 8 | Basic
|  |  |  | Relay Output 3.10 | 9 | Basic
|  |  |  | Relay Output 3.11 | 10 | Basic
|  |  |  | Relay Output 3.12 | 11 | Basic
|  |  |  | Relay Output 3.13 | 12 | Basic
|  |  |  | Relay Output 3.14 | 13 | Basic
202 | 2 | RW | MixedBits | Group MasterWatchDog (MWD) Status |  | Advanced
|  |  |  | MWD Enable | 0 | Advanced
|  |  |  | MWD Reboot Detected | 1 | Advanced
203 - 204 | 3 - 4 | RW | DWord | Counter of Digital Input 3.1 |  | Basic
205 - 206 | 5 - 6 | RW | DWord | Counter of Digital Input 3.2 |  | Basic
207 - 208 | 7 - 8 | RW | DWord | Counter of Digital Input 3.3 |  | Basic
209 - 210 | 9 - 10 | RW | DWord | Counter of Digital Input 3.4 |  | Basic
211 - 212 | 11 - 12 | RW | DWord | Counter of Digital Input 3.5 |  | Basic
213 - 214 | 13 - 14 | RW | DWord | Counter of Digital Input 3.6 |  | Basic
215 - 216 | 15 - 16 | RW | DWord | Counter of Digital Input 3.7 |  | Basic
217 - 218 | 17 - 18 | RW | DWord | Counter of Digital Input 3.8 |  | Basic
219 - 220 | 19 - 20 | RW | DWord | Counter of Digital Input 3.9 |  | Basic
221 - 222 | 21 - 22 | RW | DWord | Counter of Digital Input 3.10 |  | Basic
223 - 224 | 23 - 24 | RW | DWord | Counter of Digital Input 3.11 |  | Basic
225 - 226 | 25 - 26 | RW | DWord | Counter of Digital Input 3.12 |  | Basic
227 - 228 | 27 - 28 | RW | DWord | Counter of Digital Input 3.13 |  | Basic
229 - 230 | 29 - 30 | RW | DWord | Counter of Digital Input 3.14 |  | Basic
231 - 232 | 31 - 32 | RW | DWord | Counter of Digital Input 3.15 |  | Basic
233 - 234 | 33 - 34 | RW | DWord | Counter of Digital Input 3.16 |  | Basic
235 | 35 | W | Word | Reserved - Do Not Use |  | Reserved
236 | 36 | W | Word | Reserved - Do Not Use |  | Reserved
237 | 37 | W | Word | Reserved - Do Not Use |  | Reserved
238 | 38 | W | Word | Reserved - Do Not Use |  | Reserved
239 | 39 | RW | MixedBits | Synchronised Digital Outputs/Relay Outputs | 0 | Advanced
|  |  |  | Synchronised DO/RO 3.1 | 0 | Advanced
|  |  |  | Synchronised DO/RO 3.2 | 1 | Advanced
|  |  |  | Synchronised DO/RO 3.3 | 2 | Advanced
|  |  |  | Synchronised DO/RO 3.4 | 3 | Advanced
|  |  |  | Synchronised DO/RO 3.5 | 4 | Advanced
|  |  |  | Synchronised DO/RO 3.6 | 5 | Advanced
|  |  |  | Synchronised DO/RO 3.7 | 6 | Advanced
|  |  |  | Synchronised DO/RO 3.8 | 7 | Advanced
|  |  |  | Synchronised DO/RO 3.9 | 8 | Advanced
|  |  |  | Synchronised DO/RO 3.10 | 9 | Advanced
|  |  |  | Synchronised DO/RO 3.11 | 10 | Advanced
|  |  |  | Synchronised DO/RO 3.12 | 11 | Advanced
|  |  |  | Synchronised DO/RO 3.13 | 12 | Advanced
|  |  |  | Synchronised DO/RO 3.14 | 13 | Advanced
240 | 40 | RW | MixedBits | Synchronised Digital Output/Relay Output Locks | 0 | Advanced
|  |  |  | Synchronised DO/RO Lock 3.1 | 0 | Advanced
|  |  |  | Synchronised DO/RO Lock 3.2 | 1 | Advanced
|  |  |  | Synchronised DO/RO Lock 3.3 | 2 | Advanced
|  |  |  | Synchronised DO/RO Lock 3.4 | 3 | Advanced
|  |  |  | Synchronised DO/RO Lock 3.5 | 4 | Advanced
|  |  |  | Synchronised DO/RO Lock 3.6 | 5 | Advanced
|  |  |  | Synchronised DO/RO Lock 3.7 | 6 | Advanced
|  |  |  | Synchronised DO/RO Lock 3.8 | 7 | Advanced
|  |  |  | Synchronised DO/RO Lock 3.9 | 8 | Advanced
|  |  |  | Synchronised DO/RO Lock 3.10 | 9 | Advanced
|  |  |  | Synchronised DO/RO Lock 3.11 | 10 | Advanced
|  |  |  | Synchronised DO/RO Lock 3.12 | 11 | Advanced
|  |  |  | Synchronised DO/RO Lock 3.13 | 12 | Advanced
|  |  |  | Synchronised DO/RO Lock 3.14 | 13 | Advanced
| 100 - 101 | RW | DWord | (Internal) RS485 Full Mode Configuration 3.1 |  | Obsolete
700 | 500 | W | Word | Reserved - Do Not Use |  | Reserved
701 | 501 | W | Word | Reserved - Do Not Use |  | Reserved
702 | 502 | W | Word | Reserved - Do Not Use |  | Reserved
703 | 503 | W | Word | Reserved - Do Not Use |  | Reserved
704 | 504 | W | Word | Reserved - Do Not Use |  | Reserved
705 | 505 | W | Word | Reserved - Do Not Use |  | Reserved
706 | 506 | W | Word | Reserved - Do Not Use |  | Reserved
707 | 507 | W | Word | Reserved - Do Not Use |  | Reserved
708 | 508 | W | Word | Reserved - Do Not Use |  | Reserved
709 | 509 | W | Word | Reserved - Do Not Use |  | Reserved
| 510 | RW | Word | (Internal) Stored Firmware Version |  | Expert
| 511 | RW | Word | (Internal) Stored Firmware Revision |  | Expert
| 512 | RW | Word | (Internal) Stored Base Firmware Revision |  | Expert
| 513 | RW | Word | (Internal) Stored Expanded Flash Magic Value |  | Expert
| 514 | RW | Word | (Internal) Stored PCB Revision |  | Expert
| 515 | RW | Word | (Internal) Stored PCB Serial Number |  | Expert
| 516 | RW | Word | (Internal) Stored HW Revision Number |  | Expert
1200 | 1000 | R | Word | Firmware Version |  | Expert
1201 | 1001 | R | Word | Number of I/Os |  | Advanced
|  |  |  | Number of DIs | 0 - 7 | Advanced
|  |  |  | Number of DOs | 8 - 15 | Advanced
1202 | 1002 | R | Word | Number of peripherals |  | Advanced
|  |  |  | Number of internal RS485 lines | 0 - 3 | Advanced
|  |  |  | Number of AOs | 4 - 7 | Advanced
|  |  |  | Number of AIs | 8 - 15 | Advanced
1203 | 1003 | R | Word | Firmware ID |  | Expert
1204 | 1004 | R | Word | Hardware ID |  | Expert
1205 - 1206 | 1005 - 1006 | R | DWord | PCB Serial Number |  | Expert
1207 | 1007 | RW | Word | Interrupt Mask |  | Expert
|  |  |  | RS485 RX queue not empty | 0 | Expert
|  |  |  | RS485 TX queue empty | 1 | Expert
|  |  |  | RS485 ModBus RX frame finished | 2 | Expert
|  |  |  | Digital Input changed state | 3 | Expert
1208 | 1008 | RW | Word | Group MasterWatchDog (MWD) Timeout (in 1ms) |  | Advanced
1209 | 1009 | R | Word | VRef of MCU |  | Expert
1210 | 1010 | RW | Word | Debounce time (in 100us) for DI 3.1 |  | Advanced
1211 | 1011 | RW | Word | Debounce time (in 100us) for DI 3.2 |  | Advanced
1212 | 1012 | RW | Word | Debounce time (in 100us) for DI 3.3 |  | Advanced
1213 | 1013 | RW | Word | Debounce time (in 100us) for DI 3.4 |  | Advanced
1214 | 1014 | RW | Word | Debounce time (in 100us) for DI 3.5 |  | Advanced
1215 | 1015 | RW | Word | Debounce time (in 100us) for DI 3.6 |  | Advanced
1216 | 1016 | RW | Word | Debounce time (in 100us) for DI 3.7 |  | Advanced
1217 | 1017 | RW | Word | Debounce time (in 100us) for DI 3.8 |  | Advanced
1218 | 1018 | RW | Word | Debounce time (in 100us) for DI 3.9 |  | Advanced
1219 | 1019 | RW | Word | Debounce time (in 100us) for DI 3.10 |  | Advanced
1220 | 1020 | RW | Word | Debounce time (in 100us) for DI 3.11 |  | Advanced
1221 | 1021 | RW | Word | Debounce time (in 100us) for DI 3.12 |  | Advanced
1222 | 1022 | RW | Word | Debounce time (in 100us) for DI 3.13 |  | Advanced
1223 | 1023 | RW | Word | Debounce time (in 100us) for DI 3.14 |  | Advanced
1224 | 1024 | RW | Word | Debounce time (in 100us) for DI 3.15 |  | Advanced
1225 | 1025 | RW | Word | Debounce time (in 100us) for DI 3.16 |  | Advanced
1226 | 1026 | RW | MixedBits | Enable DirectSwitch functionality | 0 | Basic
|  |  |  | Enable DirectSwitch on DI 3.1 | 0 | Basic
|  |  |  | Enable DirectSwitch on DI 3.2 | 1 | Basic
|  |  |  | Enable DirectSwitch on DI 3.3 | 2 | Basic
|  |  |  | Enable DirectSwitch on DI 3.4 | 3 | Basic
|  |  |  | Enable DirectSwitch on DI 3.5 | 4 | Basic
|  |  |  | Enable DirectSwitch on DI 3.6 | 5 | Basic
|  |  |  | Enable DirectSwitch on DI 3.7 | 6 | Basic
|  |  |  | Enable DirectSwitch on DI 3.8 | 7 | Basic
|  |  |  | Enable DirectSwitch on DI 3.9 | 8 | Basic
|  |  |  | Enable DirectSwitch on DI 3.10 | 9 | Basic
|  |  |  | Enable DirectSwitch on DI 3.11 | 10 | Basic
|  |  |  | Enable DirectSwitch on DI 3.12 | 11 | Basic
|  |  |  | Enable DirectSwitch on DI 3.13 | 12 | Basic
|  |  |  | Enable DirectSwitch on DI 3.14 | 13 | Basic
1227 | 1027 | RW | MixedBits | Invert DirectSwitch Polarity | 0 | Basic
|  |  |  | Invert DirectSwitch Polarity on DI 3.1 | 0 | Basic
|  |  |  | Invert DirectSwitch Polarity on DI 3.2 | 1 | Basic
|  |  |  | Invert DirectSwitch Polarity on DI 3.3 | 2 | Basic
|  |  |  | Invert DirectSwitch Polarity on DI 3.4 | 3 | Basic
|  |  |  | Invert DirectSwitch Polarity on DI 3.5 | 4 | Basic
|  |  |  | Invert DirectSwitch Polarity on DI 3.6 | 5 | Basic
|  |  |  | Invert DirectSwitch Polarity on DI 3.7 | 6 | Basic
|  |  |  | Invert DirectSwitch Polarity on DI 3.8 | 7 | Basic
|  |  |  | Invert DirectSwitch Polarity on DI 3.9 | 8 | Basic
|  |  |  | Invert DirectSwitch Polarity on DI 3.10 | 9 | Basic
|  |  |  | Invert DirectSwitch Polarity on DI 3.11 | 10 | Basic
|  |  |  | Invert DirectSwitch Polarity on DI 3.12 | 11 | Basic
|  |  |  | Invert DirectSwitch Polarity on DI 3.13 | 12 | Basic
|  |  |  | Invert DirectSwitch Polarity on DI 3.14 | 13 | Basic
1228 | 1028 | RW | MixedBits | Enabled DirectSwitch Toggle | 0 | Basic
|  |  |  | Enable DirectSwitch Toggle on DI 3.1 | 0 | Basic
|  |  |  | Enable DirectSwitch Toggle on DI 3.2 | 1 | Basic
|  |  |  | Enable DirectSwitch Toggle on DI 3.3 | 2 | Basic
|  |  |  | Enable DirectSwitch Toggle on DI 3.4 | 3 | Basic
|  |  |  | Enable DirectSwitch Toggle on DI 3.5 | 4 | Basic
|  |  |  | Enable DirectSwitch Toggle on DI 3.6 | 5 | Basic
|  |  |  | Enable DirectSwitch Toggle on DI 3.7 | 6 | Basic
|  |  |  | Enable DirectSwitch Toggle on DI 3.8 | 7 | Basic
|  |  |  | Enable DirectSwitch Toggle on DI 3.9 | 8 | Basic
|  |  |  | Enable DirectSwitch Toggle on DI 3.10 | 9 | Basic
|  |  |  | Enable DirectSwitch Toggle on DI 3.11 | 10 | Basic
|  |  |  | Enable DirectSwitch Toggle on DI 3.12 | 11 | Basic
|  |  |  | Enable DirectSwitch Toggle on DI 3.13 | 12 | Basic
|  |  |  | Enable DirectSwitch Toggle on DI 3.14 | 13 | Basic
1229 | 1029 | W | Word | Reserved - Do Not Use |  | Reserved
1230 | 1030 | W | Word | Reserved - Do Not Use |  | Reserved
| 2000 - 2219 | W | Word | Reserved - Do Not Use |  | Reserved

## Coils - group 1
Neuron L203
Coils - group 1
Register Address
Via Unit 0 | Via Unit 1 | R/W | Content | Category
0 | 0 | RW | Digital Output 1.1 | Basic
1 | 1 | RW | Digital Output 1.2 | Basic
2 | 2 | RW | Digital Output 1.3 | Basic
3 | 3 | RW | Digital Output 1.4 | Basic
4 | 4 | R | Digital Input 1.1 | Basic
5 | 5 | R | Digital Input 1.2 | Basic
6 | 6 | R | Digital Input 1.3 | Basic
7 | 7 | R | Digital Input 1.4 | Basic
8 | 8 | RW | User Programmable LED 1.1 | Basic
9 | 9 | RW | User Programmable LED 1.2 | Basic
10 | 10 | RW | User Programmable LED 1.3 | Basic
11 | 11 | RW | User Programmable LED 1.4 | Basic
1000 | 1000 | RW | MWD reset indication | Advanced
1001 | 1001 | RW | Enable/Disable 1Wire Bus | Advanced
1002 | 1002 | R | Reset group MCU | Advanced
1003 | 1003 | RW | Save current configuration and use on startup | Advanced
1004 | 1004 | RW | (Internal) Firmware programming toggle | Expert
1005 | 1005 | RW | (Internal) Firmware reprogramming toggle | Expert
1006 | 1006 | RW | (Internal) Firmware calibration programming toggle | Expert
1007 | 1007 | RW | Enable DirectSwitch on DI 1.1 | Advanced
1008 | 1008 | RW | Enable DirectSwitch on DI 1.2 | Advanced
1009 | 1009 | RW | Enable DirectSwitch on DI 1.3 | Advanced
1010 | 1010 | RW | Enable DirectSwitch on DI 1.4 | Advanced
1011 | 1011 | RW | Invert DirectSwitch Polarity on DI 1.1 | Advanced
1012 | 1012 | RW | Invert DirectSwitch Polarity on DI 1.2 | Advanced
1013 | 1013 | RW | Invert DirectSwitch Polarity on DI 1.3 | Advanced
1014 | 1014 | RW | Invert DirectSwitch Polarity on DI 1.4 | Advanced
1015 | 1015 | RW | Enable DirectSwitch Toggle Mode on DI 1.1 | Advanced
1016 | 1016 | RW | Enable DirectSwitch Toggle Mode on DI 1.2 | Advanced
1017 | 1017 | RW | Enable DirectSwitch Toggle Mode on DI 1.3 | Advanced
1018 | 1018 | RW | Enable DirectSwitch Toggle Mode on DI 1.4 | Advanced

## Coils - group 2
Neuron L203
Coils - group 2
Register Address
Via Unit 0 | Via Unit 2 | R/W | Content | Category
100 | 0 | RW | Relay Output 2.1 | Basic
101 | 1 | RW | Relay Output 2.2 | Basic
102 | 2 | RW | Relay Output 2.3 | Basic
103 | 3 | RW | Relay Output 2.4 | Basic
104 | 4 | RW | Relay Output 2.5 | Basic
105 | 5 | RW | Relay Output 2.6 | Basic
106 | 6 | RW | Relay Output 2.7 | Basic
107 | 7 | RW | Relay Output 2.8 | Basic
108 | 8 | RW | Relay Output 2.9 | Basic
109 | 9 | RW | Relay Output 2.10 | Basic
110 | 10 | RW | Relay Output 2.11 | Basic
111 | 11 | RW | Relay Output 2.12 | Basic
112 | 12 | RW | Relay Output 2.13 | Basic
113 | 13 | RW | Relay Output 2.14 | Basic
114 | 14 | R | Digital Input 2.1 | Basic
115 | 15 | R | Digital Input 2.2 | Basic
116 | 16 | R | Digital Input 2.3 | Basic
117 | 17 | R | Digital Input 2.4 | Basic
118 | 18 | R | Digital Input 2.5 | Basic
119 | 19 | R | Digital Input 2.6 | Basic
120 | 20 | R | Digital Input 2.7 | Basic
121 | 21 | R | Digital Input 2.8 | Basic
122 | 22 | R | Digital Input 2.9 | Basic
123 | 23 | R | Digital Input 2.10 | Basic
124 | 24 | R | Digital Input 2.11 | Basic
125 | 25 | R | Digital Input 2.12 | Basic
126 | 26 | R | Digital Input 2.13 | Basic
127 | 27 | R | Digital Input 2.14 | Basic
128 | 28 | R | Digital Input 2.15 | Basic
129 | 29 | R | Digital Input 2.16 | Basic
1100 | 1000 | RW | MWD reset indication | Advanced
1102 | 1002 | R | Reset group MCU | Advanced
1103 | 1003 | RW | Save current configuration and use on startup | Advanced
1104 | 1004 | RW | (Internal) Firmware programming toggle | Expert
1105 | 1005 | RW | (Internal) Firmware reprogramming toggle | Expert
1106 | 1006 | RW | (Internal) Firmware calibration programming toggle | Expert
1107 | 1007 | RW | Enable DirectSwitch on DI 2.1 | Advanced
1108 | 1008 | RW | Enable DirectSwitch on DI 2.2 | Advanced
1109 | 1009 | RW | Enable DirectSwitch on DI 2.3 | Advanced
1110 | 1010 | RW | Enable DirectSwitch on DI 2.4 | Advanced
1111 | 1011 | RW | Enable DirectSwitch on DI 2.5 | Advanced
1112 | 1012 | RW | Enable DirectSwitch on DI 2.6 | Advanced
1113 | 1013 | RW | Enable DirectSwitch on DI 2.7 | Advanced
1114 | 1014 | RW | Enable DirectSwitch on DI 2.8 | Advanced
1115 | 1015 | RW | Enable DirectSwitch on DI 2.9 | Advanced
1116 | 1016 | RW | Enable DirectSwitch on DI 2.10 | Advanced
1117 | 1017 | RW | Enable DirectSwitch on DI 2.11 | Advanced
1118 | 1018 | RW | Enable DirectSwitch on DI 2.12 | Advanced
1119 | 1019 | RW | Enable DirectSwitch on DI 2.13 | Advanced
1120 | 1020 | RW | Enable DirectSwitch on DI 2.14 | Advanced
1121 | 1021 | RW | Invert DirectSwitch Polarity on DI 2.1 | Advanced
1122 | 1022 | RW | Invert DirectSwitch Polarity on DI 2.2 | Advanced
1123 | 1023 | RW | Invert DirectSwitch Polarity on DI 2.3 | Advanced
1124 | 1024 | RW | Invert DirectSwitch Polarity on DI 2.4 | Advanced
1125 | 1025 | RW | Invert DirectSwitch Polarity on DI 2.5 | Advanced
1126 | 1026 | RW | Invert DirectSwitch Polarity on DI 2.6 | Advanced
1127 | 1027 | RW | Invert DirectSwitch Polarity on DI 2.7 | Advanced
1128 | 1028 | RW | Invert DirectSwitch Polarity on DI 2.8 | Advanced
1129 | 1029 | RW | Invert DirectSwitch Polarity on DI 2.9 | Advanced
1130 | 1030 | RW | Invert DirectSwitch Polarity on DI 2.10 | Advanced
1131 | 1031 | RW | Invert DirectSwitch Polarity on DI 2.11 | Advanced
1132 | 1032 | RW | Invert DirectSwitch Polarity on DI 2.12 | Advanced
1133 | 1033 | RW | Invert DirectSwitch Polarity on DI 2.13 | Advanced
1134 | 1034 | RW | Invert DirectSwitch Polarity on DI 2.14 | Advanced
1135 | 1035 | RW | Enable DirectSwitch Toggle Mode on DI 2.1 | Advanced
1136 | 1036 | RW | Enable DirectSwitch Toggle Mode on DI 2.2 | Advanced
1137 | 1037 | RW | Enable DirectSwitch Toggle Mode on DI 2.3 | Advanced
1138 | 1038 | RW | Enable DirectSwitch Toggle Mode on DI 2.4 | Advanced
1139 | 1039 | RW | Enable DirectSwitch Toggle Mode on DI 2.5 | Advanced
1140 | 1040 | RW | Enable DirectSwitch Toggle Mode on DI 2.6 | Advanced
1141 | 1041 | RW | Enable DirectSwitch Toggle Mode on DI 2.7 | Advanced
1142 | 1042 | RW | Enable DirectSwitch Toggle Mode on DI 2.8 | Advanced
1143 | 1043 | RW | Enable DirectSwitch Toggle Mode on DI 2.9 | Advanced
1144 | 1044 | RW | Enable DirectSwitch Toggle Mode on DI 2.10 | Advanced
1145 | 1045 | RW | Enable DirectSwitch Toggle Mode on DI 2.11 | Advanced
1146 | 1046 | RW | Enable DirectSwitch Toggle Mode on DI 2.12 | Advanced
1147 | 1047 | RW | Enable DirectSwitch Toggle Mode on DI 2.13 | Advanced
1148 | 1048 | RW | Enable DirectSwitch Toggle Mode on DI 2.14 | Advanced

## Coils - group 3
Neuron L203
Coils - group 3
Register Address
Via Unit 0 | Via Unit 3 | R/W | Content | Category
200 | 0 | RW | Relay Output 3.1 | Basic
201 | 1 | RW | Relay Output 3.2 | Basic
202 | 2 | RW | Relay Output 3.3 | Basic
203 | 3 | RW | Relay Output 3.4 | Basic
204 | 4 | RW | Relay Output 3.5 | Basic
205 | 5 | RW | Relay Output 3.6 | Basic
206 | 6 | RW | Relay Output 3.7 | Basic
207 | 7 | RW | Relay Output 3.8 | Basic
208 | 8 | RW | Relay Output 3.9 | Basic
209 | 9 | RW | Relay Output 3.10 | Basic
210 | 10 | RW | Relay Output 3.11 | Basic
211 | 11 | RW | Relay Output 3.12 | Basic
212 | 12 | RW | Relay Output 3.13 | Basic
213 | 13 | RW | Relay Output 3.14 | Basic
214 | 14 | R | Digital Input 3.1 | Basic
215 | 15 | R | Digital Input 3.2 | Basic
216 | 16 | R | Digital Input 3.3 | Basic
217 | 17 | R | Digital Input 3.4 | Basic
218 | 18 | R | Digital Input 3.5 | Basic
219 | 19 | R | Digital Input 3.6 | Basic
220 | 20 | R | Digital Input 3.7 | Basic
221 | 21 | R | Digital Input 3.8 | Basic
222 | 22 | R | Digital Input 3.9 | Basic
223 | 23 | R | Digital Input 3.10 | Basic
224 | 24 | R | Digital Input 3.11 | Basic
225 | 25 | R | Digital Input 3.12 | Basic
226 | 26 | R | Digital Input 3.13 | Basic
227 | 27 | R | Digital Input 3.14 | Basic
228 | 28 | R | Digital Input 3.15 | Basic
229 | 29 | R | Digital Input 3.16 | Basic
1200 | 1000 | RW | MWD reset indication | Advanced
1202 | 1002 | R | Reset group MCU | Advanced
1203 | 1003 | RW | Save current configuration and use on startup | Advanced
1204 | 1004 | RW | (Internal) Firmware programming toggle | Expert
1205 | 1005 | RW | (Internal) Firmware reprogramming toggle | Expert
1206 | 1006 | RW | (Internal) Firmware calibration programming toggle | Expert
1207 | 1007 | RW | Enable DirectSwitch on DI 3.1 | Advanced
1208 | 1008 | RW | Enable DirectSwitch on DI 3.2 | Advanced
1209 | 1009 | RW | Enable DirectSwitch on DI 3.3 | Advanced
1210 | 1010 | RW | Enable DirectSwitch on DI 3.4 | Advanced
1211 | 1011 | RW | Enable DirectSwitch on DI 3.5 | Advanced
1212 | 1012 | RW | Enable DirectSwitch on DI 3.6 | Advanced
1213 | 1013 | RW | Enable DirectSwitch on DI 3.7 | Advanced
1214 | 1014 | RW | Enable DirectSwitch on DI 3.8 | Advanced
1215 | 1015 | RW | Enable DirectSwitch on DI 3.9 | Advanced
1216 | 1016 | RW | Enable DirectSwitch on DI 3.10 | Advanced
1217 | 1017 | RW | Enable DirectSwitch on DI 3.11 | Advanced
1218 | 1018 | RW | Enable DirectSwitch on DI 3.12 | Advanced
1219 | 1019 | RW | Enable DirectSwitch on DI 3.13 | Advanced
1220 | 1020 | RW | Enable DirectSwitch on DI 3.14 | Advanced
1221 | 1021 | RW | Invert DirectSwitch Polarity on DI 3.1 | Advanced
1222 | 1022 | RW | Invert DirectSwitch Polarity on DI 3.2 | Advanced
1223 | 1023 | RW | Invert DirectSwitch Polarity on DI 3.3 | Advanced
1224 | 1024 | RW | Invert DirectSwitch Polarity on DI 3.4 | Advanced
1225 | 1025 | RW | Invert DirectSwitch Polarity on DI 3.5 | Advanced
1226 | 1026 | RW | Invert DirectSwitch Polarity on DI 3.6 | Advanced
1227 | 1027 | RW | Invert DirectSwitch Polarity on DI 3.7 | Advanced
1228 | 1028 | RW | Invert DirectSwitch Polarity on DI 3.8 | Advanced
1229 | 1029 | RW | Invert DirectSwitch Polarity on DI 3.9 | Advanced
1230 | 1030 | RW | Invert DirectSwitch Polarity on DI 3.10 | Advanced
1231 | 1031 | RW | Invert DirectSwitch Polarity on DI 3.11 | Advanced
1232 | 1032 | RW | Invert DirectSwitch Polarity on DI 3.12 | Advanced
1233 | 1033 | RW | Invert DirectSwitch Polarity on DI 3.13 | Advanced
1234 | 1034 | RW | Invert DirectSwitch Polarity on DI 3.14 | Advanced
1235 | 1035 | RW | Enable DirectSwitch Toggle Mode on DI 3.1 | Advanced
1236 | 1036 | RW | Enable DirectSwitch Toggle Mode on DI 3.2 | Advanced
1237 | 1037 | RW | Enable DirectSwitch Toggle Mode on DI 3.3 | Advanced
1238 | 1038 | RW | Enable DirectSwitch Toggle Mode on DI 3.4 | Advanced
1239 | 1039 | RW | Enable DirectSwitch Toggle Mode on DI 3.5 | Advanced
1240 | 1040 | RW | Enable DirectSwitch Toggle Mode on DI 3.6 | Advanced
1241 | 1041 | RW | Enable DirectSwitch Toggle Mode on DI 3.7 | Advanced
1242 | 1042 | RW | Enable DirectSwitch Toggle Mode on DI 3.8 | Advanced
1243 | 1043 | RW | Enable DirectSwitch Toggle Mode on DI 3.9 | Advanced
1244 | 1044 | RW | Enable DirectSwitch Toggle Mode on DI 3.10 | Advanced
1245 | 1045 | RW | Enable DirectSwitch Toggle Mode on DI 3.11 | Advanced
1246 | 1046 | RW | Enable DirectSwitch Toggle Mode on DI 3.12 | Advanced
1247 | 1047 | RW | Enable DirectSwitch Toggle Mode on DI 3.13 | Advanced
1248 | 1048 | RW | Enable DirectSwitch Toggle Mode on DI 3.14 | Advanced

## Description
Check out the UniPi Knowledge base for more information
| Byte order | Brief protocol description: | • UniPi Neuron and Axon uses the ModBus TCP protocol to provide access to I/Os
| 0-LSB, 15-MSB |  | • ModbusTCP provides access to all I/Os except 1Wire and RS485/RS232 and other buses and serial lines
• By default the server listens only on local loopback, if needed it is possible to let it listen on all interfaces by changing its systemd script.
• ModBus word size is 16 bits
• ModBus uses big endian byte encoding
Analog Input Configuration(U/I) |  |  | • Integer variables of type Word and DWord are always unsigned, type Int is signed and corresponds to a single word
Value | Ai Mode |  | • Multiple-word values are encoded as big endian memory as well - from a little-endian perspective a 64bit byte parsing order is 78563412
0 | Voltage 0 – 10V |  | • Floating point values are encoded in the IEEE 754 half-precision format, with big-endian byte order
1 | Current 0 – 20mA |  | • Double-precision floating point values are encoded in the IEEE 754 single-precision format, with the same byte order as multi-word integers
• QModMaster is a useful tool for exploring ModBus encoding and communication
• For more information about ModBus see: http://www.simplymodbus.ca/
Analog Input Configuration(U/I/R)
Value | Ai Mode
0 | Off
1 | Voltage 0 – 10 V
2 | Voltage 0 – 2.5 V
3 | Current 0 – 20 mA
4 | Resistance (three conductors) 0 – 1 960 Ω
5 | Resistance (two conductors) 0 – 100 kΩ
Analog Output Configuration(U/I/R-measure)
Value | Type of measurement
0 | Voltage 0 – 10V
1 | Current 0 – 20mA
3 | Resistance 0 – 2kΩ
Baud rate configuration (obsolete)
Value | Speed [bps]
11 | 2400
12 | 4800
13 | 9600
14 | 19200
15 | 38400
4097 | 57600
4098 | 115200